## Summary
SWAS Thermal Feasibility & Auto-Adjustment Report
Design Basis
CW Supply Temp | 90.0 F
CW Max Flow (per cooler) | 12.0 GPM
CW Design dT | 20.0 F
CHW Supply Temp | 55.0 F
CHW Return Temp | 65.0 F
Target Sample Outlet | 77.0 F
LMTD Correction (F) | 1.0
System Results
Total Sample Points | 7
Originally Infeasible | 2
Primary T_out Adjusted | 0
Sample Flow Adjusted | 5
Total CW Duty (Btu/hr) | 282,001
Total CHW Duty (Btu/hr) | 55,030
Total Chiller Load (tons) | 4.59
Total Combined Duty (Btu/hr) | 337,031

## Point Detail
Sample Point | Phase | T_sat (F) | P (psig) | Sample T_in Primary (F) | Sample T_out Primary Orig (F) | Sample T_out Primary Adj (F) | Sample T_in Secondary (F) | Sample T_out Final (F) | Flow Original (lb/min) | Flow Adjusted (lb/min) | Flow Original (lb/hr) | Flow Adjusted (lb/hr) | CW Supply (F) | CW Return (F) | CW Flow (GPM) | CW dT Design (F) | CHW Supply (F) | CHW Return (F) | CHW Flow Req (GPM) | Q_primary Req (Btu/hr) | Q_primary Adj (Btu/hr) | Q_primary Util Max (Btu/hr) | Q_secondary Adj (Btu/hr) | Q_total (Btu/hr) | Chiller Tons | A_prim Required (ft2) | A_prim Available (ft2) | A_prim Adjusted (ft2) | A_sec Required (ft2) | A_sec Available (ft2) | Area OK | Utility OK | Primary Feasible | Secondary Feasible | Flags / Notes
Demin Water | Subcooled Liquid | 355.6 | 130 | 104 | 104 | 104 | 104 | 77 | 6.6 | 3.21 | 396 | 192.6 | 90 | 90 | 0 | 20 | 55 | 65 | 1.04 | 0 | 0 | 120096 | 5188 | 5188 | 0.43233 | 0 | 2.5 | 0 | 2.496 | 2.5 | PASS | PASS | PASS | PASS | Secondary flow solved: 6.60 -> 3.210 lb/min
Cond Pump Disch. | Subcooled Liquid | 457.4 | 440 | 100 | 100 | 100 | 100 | 77 | 6.6 | 3.553 | 396 | 213.2 | 90 | 90 | 0 | 20 | 55 | 65 | 0.98 | 0 | 0 | 120096 | 4886 | 4886 | 0.40717 | 0 | 2.5 | 0 | 2.493 | 2.5 | PASS | PASS | PASS | PASS | Secondary flow solved: 6.60 -> 3.553 lb/min
Cond Polisher Out | Subcooled Liquid | 461.7 | 460 | 100 | 100 | 100 | 100 | 77 | 6.6 | 3.553 | 396 | 213.2 | 90 | 90 | 0 | 20 | 55 | 65 | 0.98 | 0 | 0 | 120096 | 4885 | 4885 | 0.40708 | 0 | 2.5 | 0 | 2.492 | 2.5 | PASS | PASS | PASS | PASS | Secondary flow solved: 6.60 -> 3.553 lb/min
Deaerator Inlet | Subcooled Liquid | 355.1 | 129 | 281 | 105 | 105 | 105 | 77 | 6.6 | 1.56 | 396 | 93.6 | 90 | 92.8 | 12 | 20 | 55 | 65 | 0.52 | 70094 | 16568 | 120096 | 2615 | 19183 | 0.21792 | 10.5834 | 2.5 | 2.419 | 1.241 | 2.5 | FAIL | PASS | FAIL | PASS | Area Limited ¦ Temp adjustment alone insufficient — flow reduction required ¦ Adjusted Sample Flow: 6.60 -> 1.56 lb/min
Deaerator Outlet | Subcooled Liquid | 355.1 | 129 | 334 | 105 | 105 | 105 | 77 | 6.6 | 1.83 | 396 | 109.8 | 90 | 94.2 | 12 | 20 | 55 | 65 | 0.61 | 91725 | 25433 | 120096 | 3067 | 28500 | 0.25558 | 8.9944 | 2.5 | 2.412 | 1.455 | 2.5 | FAIL | PASS | FAIL | PASS | Area Limited ¦ Temp adjustment alone insufficient — flow reduction required ¦ Adjusted Sample Flow: 6.60 -> 1.83 lb/min
Main Steam Hdr | Superheated | 627.3 | 1868 | 847 | 248.7 | 248.7 | 248.7 | 77 | 1.73 | 1.73 | 103.8 | 103.8 | 90 | 110 | 12 | 20 | 55 | 65 | 3.55 | 120000 | 120000 | 120096 | 17764 | 137764 | 1.4803 | 1.817 | 3.5 | 1.817 | 2.331 | 2.5 | PASS | PASS | PASS | PASS
HRH Steam Hdr | Superheated | 427.5 | 320 | 875 | 248.7 | 248.7 | 248.7 | 77 | 1.61 | 1.61 | 96.6 | 96.6 | 90 | 110 | 12 | 20 | 55 | 65 | 3.32 | 120000 | 120000 | 120096 | 16625 | 136625 | 1.3854 | 1.785 | 3.5 | 1.785 | 2.182 | 2.5 | PASS | PASS | PASS | PASS
TOTAL | [19 empty] | 282001 | 282001 |  | 55030 | 337031 | 4.5858

## Steam Zones
Sample Point | Zone | Q (Btu/hr) | LMTD (F) | U (Btu/hr-ft2-F) | UA (Btu/hr-F) | A_required (ft2) | Note
Deaerator Inlet | Liquid | 16567.6475 | 68.48 | 100 | 241.9 | 2.419
Deaerator Inlet | TOTAL | 16567.6475 |  |  |  | 2.419
Deaerator Outlet | Liquid | 25432.9626 | 81.1 | 130 | 313.6 | 2.412
Deaerator Outlet | TOTAL | 25432.9626 |  |  |  | 2.412
Main Steam Hdr | Subcooling | 45351.7087 | 307.82 | 150 | 147.3 | 0.982
Main Steam Hdr | Condensation | 50534.15 | 525.53 | 500 | 96.2 | 0.192
Main Steam Hdr | Desuperheat | 24033.441 | 622.97 | 60 | 38.6 | 0.643
Main Steam Hdr | TOTAL | 119919.2998 |  |  |  | 1.817
HRH Steam Hdr | Subcooling | 18081.8866 | 235.77 | 150 | 76.7 | 0.511
HRH Steam Hdr | Condensation | 77186.0812 | 328.02 | 500 | 235.3 | 0.471
HRH Steam Hdr | Desuperheat | 24662.3763 | 511.71 | 60 | 48.2 | 0.803
HRH Steam Hdr | TOTAL | 119930.344 |  |  |  | 1.785